## Chp 26
General Wind Design Parameters
Ref: Chp 26, ASCE 7-10
All references are to ASCE 7-10 unless noted otherwise.
Chapter 1
Risk Cat. = | IV | (risk category; Table 1.5-1)
Chapter 26
V = | 120 | mph | (basic wind speed; Fig. 26.5-1A, B, or C)
Kd = | 0.85 |  | (directionality factor; Sec. 26.6 and Table 26.6-1)
Exp. Cat. = | C |  | (exposure category; Sec. 26.7)
Kzt = | 1 |  | (topographic factor; Sec. 26.8, Fig. 26.8-1)
G = | 0.85 |  | (gust factor; Sec. 26.9)
Enclosure = | Enclosed |  | (enclosure classification)
¦GCpi¦ = | 0.18 |  | (magnitude of internal pressure coefficient; Sec. 26,11, Fig. 26.11-1)
Building Geometry
h = | 62 | ft | (mean roof height)
| X | Y
L = | 1472 | 240 | ft | (dimension parallel to wind)
B = | 240 | 1472 | ft | (dimension perpendicular to wind)

## Chp 27
MWFRS Wind Loads on Walls and Parapets
Ref: Chp 27, ASCE 7-10
All references are to ASCE 7-10 unless noted otherwise.
Applicable to flat roof structures only (i.e. roof slope θ <= 10 deg)
Roof uplift omitted for simplicity
Exposure and Velocity Pressure |  |  |  |  | Table 26.9-1
α = | 9.5 |  | (3s gust-speed power law exponent; Table 26.9-1) |  | US customary units.
zg = | 900 |  | (nominal height of the atmospheric boundary layer; Table 26.9-1) |  | C | α | zg | â | b̂ | ᾱ | b̄ | c2 | ℓ (ft) | ε̄ | zmin
Kh = | 1.1444 |  | (velocity pressure exposure coefficcient; Table 27.3-1, Note 1) |  | B | 7 | 1200 | 1/7 | 0.84 | 1/4.0 | 0.45 | 0.3 | 320 | 1/3.0 | 30
qh = | 35.8606 | psf | (velocity pressure at mean roof height; Eqn. 27.3-1) |  | C | 9.5 | 900 | 1/9.5 | 1 | 1/6.5 | 0.65 | 0.2 | 500 | 1/5.0 | 15
[5 empty] | D | 11.5 | 700 | 1/11.5 | 1.07 | 1/9.0 | 0.8 | 0.15 | 650 | 1/8.0 | 7
Wall
1 | "Max" pressures are net demands including positive GCpi.
2 | "Min" pressures are net demands including negative GCpi.
3 | "Ext. Only" pressures do not include GCpi. These are only used when GCpi on windward and
leeward walls cancel out.
4 | When combining windward, leeward, and side pressures, they must be all "Max," all "Min,"
or all "Ext. Only."
External Coefficients
Ref: Fig. 27.4-1
Direction |  | X | Y | Use with
L/B |  | 6.1333 | 0.16304 | -
Cp | Windward | 0.8 |  | qz
| Leedward | -0.2 | -0.5 | qh
| Side | -0.7 |  | qh
Net Pressures - Story-Independent
qi = | qh; Sec. 27.4.1
pz,leeward = | deisgn wind pressure; Eqn. 27.4-1
pz,side = | deisgn wind pressure; Eqn. 27.4-1
Direction |  | X | Y | Unit
qi |  | 35.8606 |  | psf
pz,leeward | Ext. Only | -6.0963 | -15.2407 | psf
| Max | 0.35861 | -8.7858 | psf
| Min | -12.5512 | -21.6956 | psf
pz,side | Ext. Only | -21.337 |  | psf
| Max | -14.8821 |  | psf
| Min | -27.7919 |  | psf
Net Pressures - Story-Dependent
z = | story elevation
Kz = | velocity pressure exposure coefficcient; Table 27.3-1, Note 1
qz = | velocity pressure at story height; Eqn. 27.3-1
pz,windward = | deisgn wind pressure; Eqn. 27.4-1
Story |  | L2 | R | Unit
z |  | 31.5 | 62 | ft
Kz |  | 0.99239 | 1.1444 | -
qz |  | 31.0961 | 35.8606 | psf
pz,windward | Ext. Only | 21.1453 | 24.3852 | psf
| Max | 27.6002 | 30.8401 | psf
| Min | 14.6904 | 17.9303 | psf
Parapet
Ref: Sec. 27.4.5
Typical Parapet
hp = | 67 | ft | (height to top of parapet)
Kp = | 1.1633 |  | (velocity pressure exposure coefficcient; Table 27.3-1, Note 1)
qp = | 36.4509 | psf | (velocity pressure at mean roof height; Eqn. 27.3-1)
| Windward | Leeward
GCpn = | 1.5 | -1
pp = | 54.6764 | -36.4509 | psf | (combined net pressure on parapet)
Picture Frame Paramet
hp = | 72.75 | ft | (height to top of parapet)
Kp = | 1.1836 |  | (velocity pressure exposure coefficcient; Table 27.3-1, Note 1)
qp = | 37.0883 | psf | (velocity pressure at mean roof height; Eqn. 27.3-1)
| Windward | Leeward
GCpn = | 1.5 | -1
pp = | 55.6324 | -37.0883 | psf | (combined net pressure on parapet)

## Chp 29
MWFRS Wind Loads on Rooftop Components
Ref: Chp 29, ASCE 7-10
All references are to ASCE 7-10 unless noted otherwise.
Penthouse and Mechanical Platform
Ref: Sec. 29.5, Fig. 29.5-1
Assume wind normal to face and rectangular section.
z = | element centroid height above grade (ft)
Kz = | velocity pressure exposure coefficcient; Table 27.3-1, Note 1
qz = | velocity pressure at mean roof height; Eqn. 27.3-1
h = | height of element (not height from grade)
D = | min horizontal dimension of element
Cf = | force coefficient from Fig 29.5-1 interpolated based on h/D
F/Af = | design wind pressure (psf)
Element | z | Kz | qz | h | D | h/D | Cf | F/Af
PH1 | 68.7083 | 1.1695 | 36.6446 | 15.4167 | 25 | 0.61667 | 1.3 | 40.4923
PH2 | 68.7083 | 1.1695 | 36.6446 | 15.4167 | 13 | 1.1859 | 1.3031 | 40.5888
Waffle slab | 71 | 1.1776 | 36.8986 | 3.5 | 12 | 0.29167 | 1.3 | 40.773
Chiller | 77 | 1.1979 | 37.5342 | 8.5 | 10 | 0.85 | 1.3 | 41.4753
Chiller
L = | 56 | ft | (length of chiller)
Px = | 3.5254 | k | (point load per chiller in X direction to be applied in ETABS)
Py = | 19.7423 | k | (point load per chiller in Y direction to be applied in ETABS)
Waffle Slab
w = | 142.7055 | plf | (line load to be applied in ETABS)
Penthouse Parapet
Ref: Sec. 29.5, Sec. 27.4.5
hp = | 76.9167 | ft | (height to top of parapet)
Kp = | 1.1976 |  | (velocity pressure exposure coefficcient; Table 27.3-1, Note 1)
qp = | 37.5257 | psf | (velocity pressure at mean roof height; Eqn. 27.3-1)
| Windward | Leeward
GCpn = | 1.5 | -1
pp = | 56.2885 | -37.5257 | psf | (combined net pressure on parapet)